## Slide 1
A Pilot Study on the Integration of Anaerobic Pre-Treatment into Existing Wastewater Treatment Plants in Jordan: Preliminary Results
I.Al-Zreiqat, M. Barjenbruch, M. Halalsheh, G. Kassab
Dead Sea, 5th. May 2025

## Slide 2: Energy and water quality Challenges and opportunities
Aim: Improving the energy use at the wastewater treatment plant
  Advanced removal of pollutants (Future requirements for Jordanian regulation)
  High energy demand for treatment and water reuse
Reasons for energy optimization
  Run empty of fossil resources
  Energy crises
  Climate change
    Increase of CO2-Emissions
    Increase in temperature
  Saving operational costs
Approaches
  Utilizing energy embedded in wastewater (Anaerobic pre-treatment at the upstream of wastewater utilities)
Notes: Bild 1 BUND Kinderseite; Bild 2 NTV

## Slide 3: Energy distribution diagram Example: Activated Sludge Process
Chart: 
| mechanical cleaning stage | biological treatment stage | secondary clarifier | posttreatment | premises | other
 | 113190.424 | 3193461.2798 | 36129.9811 | 15591.3305 | 225195.2 | 915810.6334
Notes: Beispiel: Audit Grevesmühlen

## Slide 4: ANAJO Project: Overview Period: 01.01.2022 – 31.08.2025
ANAJO: Wastewater treatment plants in the MENA-Region: Anaerobic pre-treatment to increase energy efficiency and performance of WWTPs in Jordan.
Aim: Developing a novel, climate-friendly anaerobic technology for the treatment of municipal wastewater in combination with a further treatment stage (anaerobic-aerobic).
Objectives:
  Reducing energy demand by incorporating an upstream anaerobic treatment process into the existing plants.
  Demonstrating potentials of energy production from using the embedded energy in wastewater.
  Reducing operational cost of the existing plants.
  Improving sludge management

## Slide 5: Partner
Funded by: BMUV
Germany
Jordan

## Slide 6: Pilotanlage: Process Scheme
Bluebox
RT:2min.
PT:5min.
Recirculation rate
Hz
Notes: Wastewater is pumped to the receving tank of the pilot plant (Vorlage Behälter). The feeding pump to the UASB reactor has a constant flow of around 571 Liter/hr. It runs in an ON/Off Mode. The Upflow velocity is controlled through the recirculation pump Water from the UASB reactor is further treated in the activated sludge tank. Water Quality is measured at three different points along the treatment process. The water quality is measured for the following parameters: COD, CODsol., TSS, TN, NH4-N, NO3-N, pH, Temperature.
Organic loading rate design: 3.5 kg COD/m3
Q design: 340 Liter/h
Volume UASB: 2,38 m3
Reactor hight: 2,5
Diameter: 1.1 m

## Slide 7: Transport and Installation: Site preparation

## Slide 8: Installation of the pilot plant at Abu-Nusier WWTP

## Slide 9: Connecting the pilot plant to Abu-Nusier WWTP

## Slide 10: System’s components Activated sludg- and settling tank

## Slide 11: System components UASB reactor

## Slide 12: Control and measuring system

## Slide 13: Sicherheitsmaßnahmen u. weitere Ausrüstungen

## Slide 14: Preliminary Results from the UASB reactor
Chart: Samples
CODinf._UASB | 469 | 752 | 1010 | 911 | 840 | 1019 | 1194 | 1055 | 886 | 976 | 1223 | 586 | 1278 | 1060 | 945 | 949 | 913 | 1083 | 1092 | 964 | 1324 | 1033 | 923 | 854 | 1045 | 503 | 467 | 840
CODeff._UASB | 263 | 316 | 349 | 391 | 364 | 378 | 587 | 397 | 381 | 362 | 409 | 399 | 441 | 345 | 368 | 443 | 347 | 305 | 344 | 337 | 358 | 334 | 349 | 380 | 284 | 354 | 359 | 326
Parameter | Unit | Min. | Max. | Median | Average
CODinf._UASB | [mg/l] | 467 | 1324 | 956,5 | 936
CODinf._sol._UASB | [mg/l] | 218 | 659 | 465,5 | 447
CODeff.._UASB | [mg/l] | 263 | 587 | 360,5 | 367
CODeff._sol.._UASB | [mg/l] | 115 | 371 | 149 | 156
Gas production | [l/hr] | 3 | 52 | 24 | 24

## Slide 15: TS Profile in UASB
25885 mg/l
15278 mg/l
10570 mg/l
1821 mg/l
864 mg/l
30 cm
Chart: 
| 0 | 30 | 60 | 90 | 85 | 115
TSS mg/L | 33430 | 25885 | 15278 | 10570 | 1821 | 864
60 cm
90 cm
170 cm
210 cm

## Slide 16: Energy Production from Biogas USAB Reactor as a Pre-Treatment Unit
Abu Nusier wastewater treatment plant data for 2020
  Flow= 3.947,75 m3/d
  CODCH4= Qavr. × [(So – S.) − Yobs × So)]
  So, avg.=1,011 kg COD/m3
  Savg.= 0,441 kg COD/m3
Yobs= Solid yields coefficient 0,11 kg Sludge/kg COD applied
CODCH4= 1.811,18 m3 CH4/d
QCH4= 694 m3/d
Estimated Energy=6.919 kWh/d

## Slide 17: Benefits and sustainability aspects of integrating UASB reactor into the AS systems
Fundamental lower energy demand (no aeration) in combination with the reduction of operational costs
Generating usable energy in the form of biogas
  Increasing energy prices let anaerobic technology boost
High specific loading is possible
  Small reactors are needed
  Small space demand (footprint)
Very low excess sludge production in relation to aerobic treatment with a better dewaterability
  Less pollution in landfills and the environment
Reduction of greenhouse gases
New possibilities in the design of WWTP
  Large plants (new or overloaded), but also rural areas
  Improved effluent values

## Slide 18: Summary
Meeting new effluent limits and strict water quality standards increases the operational cost of the WWTP.
Operating of activated sludge system is attributed with high energy costs
Increasing the share of renewable energy in operating the wastewater treatment plants (Hydropower and biogas, and other renewable options) reduces the energy cost of the WWTPs.
Integrating an anaerobic unit at the upstream of the biological treatmen tstage increases energy production and improves effluent water quality
The insights gained from the ongoing research project „ANAJO“ aim to assist the water authorities in its decision-making processes.

## Slide 19
Sewage treatment plants = municipal energy consumer No. 1
1. Step: Reduce energy consumption in the aeration tank. (by reducing the organic load)
2. Step: Options to increase energy production
through utilizing biogas (Anaerobic pretreatment / co-digestion)
but: Sewage treatment plants should mainly
purify wastewater and stick to discharge regulation and standards!
[Nach Schröder, 2008]
Notes: Kläranlagen von der BSR..(optional)

## Slide 20: Thank you for your attention